## SENSORS
SensorId | Name | Max | On | Type | Interface | Color | Hardware | Index | Flag
remotesensor_1433931027 | "BESS DC Voltage" | 60 | on | Voltage | rio:battery_1433930886:BATTERY_VOLTAGE | blue_2 | remotesensor | 1 | Y
remotesensor_1433931057 | "State Of Charge" | 100 | on | Percent | rio:battery_1433930886:SOC | green_1 | remotesensor | 1 | Y
remotesensor_1433931085 | "State Of Health" | 100 | on | Percent | rio:battery_1433930886:SOH | grey_2 | remotesensor | 1 | N
remotesensor_1433931109 | "BESS Avg. Cell Temp." | 100 | on | Temperature | rio:battery_1433930886:AVG_CELLTEMP | skycolor_3 | remotesensor | 1 | Y
remotesensor_1433931367 | "Max. Charge/Phase" | 4600 | on | Energy | rio:battery_1433930886:MAX_CHARGE_POWER | grey_1 | remotesensor | 1 | N
remotesensor_1433931386 | "Max. Discharge/Phase" | 4600 | on | Energy | rio:battery_1433930886:MAX_DISCHARGE_POWER | skycolor_2 | remotesensor | 1 | N
impulsesensor_1447936013 | "Wind Speed S" | 20 | on | Speed_ms | DI_1 | skycolor_6 | Impulse | 1 | Y
impulsesensor_1447936042 | "Wind Speed E" | 20 | on | Speed_ms | DI_2 | skycolor_6 | Impulse | 1 | Y
impulsesensor_1447936079 | "Wind Speed W" | 20 | on | Speed_ms | DI_3 | skycolor_6 | Impulse | 1 | Y
buscounter_1447943847 | "Solar Irradiance S" | 1200 | on | Global_Radiation | 2_1_SiRS485-MB | yellow_2 | buscounter | 1 | Y
buscounter_1447944046 | "S-Irr. Sensor-Temp." | 100 | on | Temperature | 2_1_SiRS485-MB | purple_6 | buscounter | 1
buscounter_1448468309 | "Solar Irradiance E" | 1200 | on | Global_Radiation | 2_2_SiRS485-MB | yellow_2 | buscounter | 1
buscounter_1448468376 | "E-Irr. Sensor-Temp." | 100 | on | Temperature | 2_2_SiRS485-MB | purple_6 | buscounter | 1
buscounter_1448468659 | "Solar Irradiance W" | 1200 | on | Global_Radiation | 2_3_SiRS485-MB | yellow_2 | buscounter | 1
buscounter_1448468683 | "W-Irr. Sensor-Temp." | 100 | on | Temperature | 2_3_SiRS485-MB | purple_6 | buscounter | 1
remotesensor_1448533841 | "PV Mod. Temp. E" | 100 | on | Temperature | rio:remoteio_1448533600:E20000069FF53A28 | skycolor_4 | remotesensor | 1
remotesensor_1448533863 | "PV Mod. Temp. S" | 100 | on | Temperature | rio:remoteio_1448533600:7B000006729A1D28 | skycolor_4 | remotesensor | 1
remotesensor_1448533882 | "Ambient Temp." | 100 | on | Temperature | rio:remoteio_1448533600:EF0000067B0A0828 | blue_6 | remotesensor | 1
remotesensor_1448533897 | "PV Mod. Temp. W" | 100 | on | Temperature | rio:remoteio_1448533600:AF000006A07B4828 | skycolor_4 | remotesensor | 1
remotesensor_1464342260 | "BESS Avg. Cell Voltage" | 60 | on | Voltage | rio:battery_1433930886:AVG_CELL_VOLTAGE | skycolor_3 | remotesensor | 1
remotesensor_1464342438 | "BESS Max. Cell Voltage" | 60 | on | Voltage | rio:battery_1433930886:MAX_CELL_VOLTAGE | skycolor_4 | remotesensor | 1
remotesensor_1464342638 | "BESS Min. Cell Voltage" | 60 | on | Voltage | rio:battery_1433930886:MIN_CELL_VOLTAGE | skycolor_2 | remotesensor | 1
remotesensor_1464342882 | "BESS Max. Cell Temp." | 100 | on | Temperature | rio:battery_1433930886:MAX_CELLTEMP | skycolor_4 | remotesensor | 1
remotesensor_1464343055 | "BESS Min. Cell Temp." | 100 | on | Temperature | rio:battery_1433930886:MIN_CELLTEMP | skycolor_2 | remotesensor | 1
calculationcounter_1464775062 | "Max. Charge Power" | 13800 | on | Energy |  | grey_1 | CounterCalculation | 1
calculationcounter_1464775142 | "Max. Discharge Power" | 13800 | on | Energy |  | skycolor_2 | CounterCalculation | 1
calculationcounter_1464794490 | "Stored Energy" | 26000 | on | Energy |  | green_1 | CounterCalculation | 1
calculationcounter_1464949529 | "PV Solar Radiation" | 500000 | on | Energy |  | yellow_2 | CounterCalculation | 1
calculationcounter_1464949779 | "Avg. PV Temp." | 100 | on | Temperature |  | skycolor_4 | CounterCalculation | 1
calculationcounter_1464949865 | "Avg. Wind Speed" | 20 | on | Speed_ms |  | skycolor_6 | CounterCalculation | 1
calculationcounter_1464952299 | "PV Efficiency" | 15 | on | Percent |  | yellow_1 | CounterCalculation | 1
calculationcounter_1464952362 | "PV Rated Power" | 100 | on | Percent |  | yellow_3 | CounterCalculation | 1
calculationcounter_1464952433 | "PV Self-Consumption" | 100 | on | Percent |  | blue_1 | CounterCalculation | 1
calculationcounter_1464952827 | "PV To Storage Quota" | 100 | on | Percent |  | skycolor_5 | CounterCalculation | 1
calculationcounter_1464952894 | "SYS Self-Consumption" | 100 | on | Percent |  | blue_2 | CounterCalculation | 1
calculationcounter_1464952955 | "PV Self-Sufficiency" | 100 | on | Percent |  | green_1 | CounterCalculation | 1
calculationcounter_1464953047 | "SYS Self-Sufficiency" | 100 | on | Percent |  | green_5 | CounterCalculation | 1
calculationcounter_1464953116 | "PV Over-Prod. Index" | 100 | on | Percent |  | purple_3 | CounterCalculation | 1
calculationcounter_1464953197 | "SYS Over-Prod. Index" | 100 | on | Percent |  | purple_6 | CounterCalculation | 1
remotesensor_1464971341 | "BESS Power Request/Phase" | 4600 | on | Energy | rio:battery_1433930886:REQUEST_POWER | grey_1 | remotesensor | 1
calculationcounter_1465293743 | "BESS Power Request" | 13800 | on | Energy |  | skycolor_2 | CounterCalculation | 1
remotesensor_1482412917 | "BESS DC Current" | 300 | on | Ampere | rio:battery_1433930886:BATTERY_CURRENT | blue_6 | remotesensor | 1
calculationcounter_1512666308 | "BESS PCS Charge Eff." | 100 | on | Percent |  | purple_6 | CounterCalculation | 1
calculationcounter_1512666427 | "BESS PCS Discharge Eff." | 100 | on | Percent |  | yellow_5 | CounterCalculation | 1
calculationcounter_1512666503 | "BESS Self-Sufficiency" | 100 | on | Percent |  | skycolor_2 | CounterCalculation | 1

## REGULATIONS
SensorId | Name | Max | On | Type | Interface | Color | Hardware | Index | Flag
regulation_1433940617 | "Man. BESS Pwr/Ph" | 4600 | on | ManualValue | DO_VIRTUAL |  |  | 6
regulation_1464771821 | "SYS Over-Prod./Phase" | 20000 | on | Calculation | DO_VIRTUAL |  |  | 6
regulation_1464771886 | "SYS Over-Cons./Phase" | 4600 | on | Calculation | DO_VIRTUAL |  |  | 6
regulation_1465294333 | "Man. BESS Power" | 13800 | on | Calculation | DO_VIRTUAL |  |  | 6

## COUNTERS
SensorId | Name | Hardware | Type | Max | On | Color | Index | Interface | "PAC Multiplicator" | "PAC Offset" | Parameter | Inverters | "Counter 1" | "Counter 2" | Operation | Flag
buscounter_1433927661 | "Grid Feed" | buscounter | Energy | 65000 | on | green_1 | 1 | 1_1_EASTRON-SDM630 | 1000 | 0
buscounter_1433927776 | "Grid Consumption" | buscounter | Energy | 65000 | on | red_2 | 1 | 1_1_EASTRON-SDM630 | 1000 | 0
remotecounter_1433930990 | "AC Power To Storage" | remotecounter | Energy | 13800 | on | purple_6 | 1 | rio:battery_1433930886:CHARGE_POWER |  | 0
remotecounter_1433931005 | "AC Power From Storage" | remotecounter | Energy | 13800 | on | yellow_5 | 1 | rio:battery_1433930886:DISCHARGE_POWER |  | 0
buscounter_1447923240 | "PV Production" | buscounter | Energy | 65000 | on | yellow_1 | 1 | 1_2_EASTRON-SDM630 | 1000 | 0
arithmetic_1464700679 | "Total Generation" | arithmetic | Energy | 65000 | on | yellow_2 | 1 |  |  | 0 |  |  | buscounter_1447923240 | remotecounter_1433931005 | plus
arithmetic_1464947507 | "Generation and Grid Consumption" | arithmetic | Energy | 65000 | on | green_4 | 1 |  |  | 0 |  |  | arithmetic_1464700679 | buscounter_1433927776 | plus
arithmetic_1464947575 | "Stored Energy and Grid Feed" | arithmetic | Energy | 65000 | on | red_3 | 1 |  |  | 0 |  |  | remotecounter_1433930990 | buscounter_1433927661 | plus
arithmetic_1464947681 | "Load Consumption" | arithmetic | Energy | 65000 | on | grey_1 | 1 |  |  | 0 |  |  | arithmetic_1464947507 | arithmetic_1464947575 | minus
arithmetic_1464947767 | "Total Usage" | arithmetic | Energy | 65000 | on | red_5 | 1 |  |  | 0 |  |  | arithmetic_1464947681 | remotecounter_1433930990 | plus
arithmetic_1464947853 | Self-Usage | arithmetic | Energy | 65000 | on | purple_3 | 1 |  |  | 0 |  |  | arithmetic_1464700679 | buscounter_1433927661 | minus
arithmetic_1464947907 | "PV Over-Production" | arithmetic | Energy | 65000 | on | purple_2 | 1 |  |  | 0 |  |  | buscounter_1447923240 | arithmetic_1464947681 | minus
arithmetic_1464948096 | "Storage To Grid" | arithmetic | Energy | 13800 | on | purple_3 | 1 |  |  | 0 |  |  | remotecounter_1433931005 | arithmetic_1465391383 | minus
arithmetic_1464948147 | "Storage To Loads" | arithmetic | Energy | 13800 | on | green_4 | 1 |  |  | 0 |  |  | remotecounter_1433931005 | arithmetic_1464948096 | minus
arithmetic_1464948247 | "Grid To Storage" | arithmetic | Energy | 13800 | on | purple_2 | 1 |  |  | 0 |  |  | remotecounter_1433930990 | buscounter_1447923240 | minus
arithmetic_1464948298 | "Grid To Loads" | arithmetic | Energy | 65000 | on | red_5 | 1 |  |  | 0 |  |  | buscounter_1433927776 | arithmetic_1464948247 | minus
arithmetic_1464948435 | "PV To Loads" | arithmetic | Energy | 65000 | on | skycolor_3 | 1 |  |  | 0 |  |  | buscounter_1447923240 | arithmetic_1465551783 | minus
arithmetic_1464948480 | "PV To Storage" | arithmetic | Energy | 13800 | on | yellow_4 | 1 |  |  | 0 |  |  | remotecounter_1433930990 | arithmetic_1464948247 | minus
arithmetic_1464948590 | "PV To Grid" | arithmetic | Energy | 65000 | on | green_4 | 1 |  |  | 0 |  |  | buscounter_1433927661 | arithmetic_1464948096 | minus
arithmetic_1465391383 | "Loads Over-Consumption" | arithmetic | Energy | 65000 | on | grey_2 | 1 |  |  | 0 |  |  | arithmetic_1464947681 | buscounter_1447923240 | minus
arithmetic_1465551783 | "PV To Storage and Grid" | arithmetic | Energy | 65000 | on | green_6 | 1 |  |  | 0 |  |  | arithmetic_1464948480 | arithmetic_1464948590 | plus
arithmetic_1465552010 | Self-Consumption | arithmetic | Energy | 65000 | on | blue_1 | 1 |  |  | 0 |  |  | arithmetic_1464948435 | arithmetic_1464948147 | plus
calculationcounter_1512665129 | NULL | CounterCalculation | Energy | 350 | on | grey_1 | 1 |  |  | 0
calculationcounter_1512665488 | "BESS DC Current Counter" | CounterCalculation | Energy | 350 | on | blue_6 | 1 |  |  | 0
arithmetic_1512665557 | "BESS DC Charge Current" | arithmetic | Energy | 350 | on | blue_6 | 1 |  |  | 0 |  |  | calculationcounter_1512665129 | calculationcounter_1512665488 | minus
arithmetic_1512665759 | "BESS DC Discharge Current" | arithmetic | Energy | 350 | on | blue_6 | 1 |  |  | 0 |  |  | calculationcounter_1512665488 | calculationcounter_1512665129 | minus
calculationcounter_1512666064 | "DC Power To Storage" | CounterCalculation | Energy | 15000 | on | purple_6 | 1 |  |  | 0
calculationcounter_1512666133 | "DC Power From Storage" | CounterCalculation | Energy | 15000 | on | yellow_5 | 1 |  |  | 0